## Input Sheet
Plant Performance Audit-1
ONGC Tripura Power Company Limited (OTPC)
2X363.3 MW Combined Cycle Power Plant, Tripura, India
CC Output and Heat Rate Correction Curve up to 200000 FFH provided by OTPC
Correction Factor Calculations for CC Output and Heat Rate based on correction curve provided by OTPC up to 200000 FFH
The correction factor output results estimated here in the below table-2 are based on the combined cycle output and heat rate correction curve up to 200000 FFH provided by OTPC. Black & Veatch does not guarantee the accuracy of the information, data, or results contained herein.
Table-1: Plant Input | [5 empty] | Legend:
GT | No. of MIs completed | 1st MI FFH | 2nd MI FFH | 3rd MI FFH | Current FFH | Blue Text - Dynamic Inputs - To be entered manually based on plant data
GT-1 | 1 | 56950.2 | 0 | 0 | 69881.3 | Green Text - Output Results based on correction curve provided by OTPC
GT-2 | 1 | 55489.8 | 0 | 0 | 60343.7
Table-2: CC Degradation Factor based on the Curve
Degradation |  | GT-1 | GT-2
Heat Rate Degradation Factor |  | 1.4675 | 1.0443
Heat Rate Degradation Correction Factor |  | 0.98532 | 0.98956

## Input 1_ Calculation Sheet
Plant Performance Audit-1
ONGC Tripura Power Company Limited (OTPC)
2X363.3 MW Combined Cycle Power Plant, Tripura, India
Actual CC Output and Heat Rate Correction Curves up to 200000 FFH provided by OTPC
Degradation curve in Table form: |  |  | GT-1 | [10 empty] | GTs | MIs
[10 empty] | GT | MIs |  |  | GT-1 | 0
GT Fired Hours | Output Degradation | HR degradation | Input Data | [6 empty] | GT-1 | 0 |  |  | GT-2 | 1
0 | 0 | 0 | GTs | No. of MIs completed | 1st MI FFH | 2nd MI FFH | 3rd MI FFH | Current FFH |  | GT-2 | 1 |  |  |  | 2
1810 | 1.0147 | 0.2454 | GT-1 | 1 | 56950.2 | 0 | 0 | 69881.3 | 0 |  | 2 |  |  |  | 3
4160 | 1.4873 | 0.4734 | [8 empty] | 3
6880 | 1.7849 | 0.6666 | Output Calculations
9220 | 2.0125 | 0.71978 | FFH Before 1st MI | FFH after 1st MI | FFH after 2nd MI | FFH after 3rd MI | Current FFH
12330 | 2.2577 | 0.8603 | 56950.2 | 12931.1 | 69881.3 | 69881.3 | 69881.3
13690 | 2.3803 | 0.9659 |  | 69881.3 | 69881.3 | 69881.3
16790 | 2.573 | 1.0715 | [6 empty] | Performance Reset after MI as per Curve
19120 | 2.6956 | 1.1595 | Output Results | [5 empty] | 1st MI | Output reset |  | 2.3
21650 | 2.8708 | 1.2652 | No of MIs completed | Heat Rate Degradation Factor |  | Output Degradation Factor |  |  |  | Heatrate reset |  | 1.7521
23390 | 2.9584 | 1.3357 | 1 | 1.4675 |  | 3.2922 |  |  | 2nd MI | Output reset |  | 2.4
26500 | 3.1161 | 1.4415 | [7 empty] | Heatrate reset |  | 1.6
28820 | 3.2213 | 1.512 | GT Fired Hours | Output Degradation | HR degradation |  |  |  | 3rd MI | Output reset |  | 2.4
31730 | 3.3615 | 1.6353 | 0 | 0 | 0 |  |  |  |  | Heatrate reset |  | 1.6
33860 | 3.4317 | 1.7058 | 1810 | 1.0147 | 0.2454
36390 | 3.5893 | 1.7765 | 4160 | 1.4873 | 0.4734 | [7 empty] | Degradation Curve based on MI Hours
38130 | 3.642 | 1.8821 | 6880 | 1.7849 | 0.6666
40850 | 3.7472 | 1.9702 | 9220 | 2.0125 | 0.7197 |  |  |  | GT-1
42790 | 3.8523 | 2.0408 | 12330 | 2.2577 | 0.8603
45310 | 3.98 | 2.1638 | 13690 | 2.3803 | 0.9659 |  |  |  | Degradation Curve Reset Calculation |  | Degradation Factor wrt MI
47760 | 4.08 | 2.2 | 16790 | 2.573 | 1.0715
48000 | 4.1 | 2.2521 | 19120 | 2.6956 | 1.1595 |  |  |  | After 1st MI |  | Before MI
48000 | 3.7423 | 1.5 | 21650 | 2.8708 | 1.2652 |  |  |  | Output | Heat Rate | Output | Heat Rate
48000 | 1.8 | 0.5 | 23390 | 2.9584 | 1.3357 |  |  |  | 56000 | 56000 | 56000 | 56000
50010 | 1.9812 | 0.7661 | 26500 | 3.1161 | 1.4415 |  |  |  | 60000 | 60000 | 60000 | 60000
52740 | 2.2964 | 0.8716 | 28820 | 3.2213 | 1.512 |  |  |  | 4.442 | 2.4321 | 4.442 | 2.4321
55650 | 2.5065 | 0.9772 | 31730 | 3.3615 | 1.6353 |  |  |  | 4.556 | 2.5221 | 4.556 | 2.5221
57790 | 2.6817 | 1.0828 | 33860 | 3.4317 | 1.7058 |  |  |  | 4.4691 | 2.4535 | 4.4691 | 2.4535
60120 | 2.8743 | 1.2233 | 36390 | 3.5893 | 1.7765 |  |  |  | After 2nd MI |  | After 1st MI
62450 | 3.0144 | 1.3464 | 38130 | 3.642 | 1.8821 |  |  |  | Output | Heat Rate | Output | Heat Rate
65370 | 3.2246 | 1.4345 | 40850 | 3.7472 | 1.9702 |  |  |  | 12120 | 12120 | 12120 | 12120
67310 | 3.3647 | 1.5927 | 42790 | 3.8523 | 2.0408 |  |  |  | 14450 | 14450 | 14450 | 14450
69840 | 3.5399 | 1.6984 | 45310 | 3.98 | 2.1638 |  |  |  | 3.2434 | 1.4247 | 3.2434 | 1.4247
72360 | 3.6626 | 1.7516 | 47760 | 4.08 | 2.2 |  |  |  | 3.3835 | 1.5478 | 3.3835 | 1.5478
74690 | 3.8027 | 1.9269 | 48000 | 4.1 | 2.2521 |  |  |  | 3.2922 | 1.4675 | 3.2922 | 1.4675
77400 | 3.8904 | 2.0151 | 52000 | 4.268 | 2.3421 |  |  |  | After 3rd MI |  | After 2nd MI
79540 | 4.0481 | 2.1032 | 56000 | 4.442 | 2.4321 |  |  |  | Output | Heat Rate | Output | Heat Rate
81480 | 4.1357 | 2.2088 | 60000 | 4.556 | 2.5221 |  |  |  | 65000 | 65000 | 65000 | 65000
84380 | 4.2409 | 2.2446 | 64000 | 4.69 | 2.6121 |  |  |  | 70000 | 70000 | 70000 | 70000
86710 | 4.3286 | 2.3152 | 68000 | 4.884 | 2.7021 |  |  |  | 4.4522 | 2.4475 | 4.4522 | 2.4475
89230 | 4.4163 | 2.4033 | 70000 | 4.968 | 2.7921 |  |  |  | 4.6722 | 2.5775 | 4.6722 | 2.5775
91360 | 4.504 | 2.4213 | After 1st MI |  |  | Output Difference | Heat Rate Difference |  | 4.6669 | 2.5744 | 4.6669 | 2.5744
93880 | 4.5916 | 2.5094 | 0 | 2.1691 | 0.70138 | [5 empty] | After 3rd MI
95770 | 4.6431 | 2.6 | 2010 | 2.3503 | 0.96748 | 0.1812 | 0.2661 |  |  |  | Output | Heat Rate
96000 | 4.7 | 2.605 | 4740 | 2.6655 | 1.073 | 0.3152 | 0.1055 |  |  |  | 65000 | 65000
96000 | 3 | 1 | 7650 | 2.8756 | 1.1786 | 0.2101 | 0.1056 |  |  |  | 70000 | 70000
96000 | 2.3 | 1 | 9790 | 3.0508 | 1.2842 | 0.1752 | 0.1056 |  |  |  | 5.6169 | 3.4944
98780 | 2.6854 | 1.3393 | 12120 | 3.2434 | 1.4247 | 0.1926 | 0.1405 |  |  |  | 5.7169 | 3.6144
99960 | 2.8779 | 1.4979 | 14450 | 3.3835 | 1.5478 | 0.1401 | 0.1231 |  |  |  | 5.7146 | 3.6116
104810 | 3.1932 | 1.6739 | 17370 | 3.5937 | 1.6359 | 0.2102 | 0.0881 |  |  |  | Results
108500 | 3.421 | 1.9377 | 19310 | 3.7338 | 1.7941 | 0.1401 | 0.1582 |  |  |  | Output Degradation
114510 | 3.7189 | 2.2367 | 21840 | 3.909 | 1.8998 | 0.1752 | 0.1057 |  |  |  | 0 | 4.4691
120330 | 4.0168 | 2.4482 | 24360 | 4.0317 | 1.953 | 0.1227 | 0.0532 |  |  |  | 1 | 3.2922
126740 | 4.4022 | 2.6599 | 26690 | 4.1718 | 2.1283 | 0.1401 | 0.1753 |  |  |  | 2 | 4.6669
132170 | 4.6301 | 2.8186 | 29400 | 4.2595 | 2.2165 | 0.0877 | 0.0882 |  |  |  | 3 | 5.7146
136630 | 4.8579 | 2.9 | 31540 | 4.4172 | 2.3046 | 0.1577 | 0.0881
139150 | 4.9631 | 2.98 | 33480 | 4.5048 | 2.4102 | 0.0876 | 0.1056 |  |  |  | HR Degradation
143850 | 5.15 | 3.1 | 36380 | 4.61 | 2.446 | 0.1052 | 0.0358 |  |  |  | 0 | 2.4535
144000 | 5.2 | 3.1 | 38710 | 4.6977 | 2.5166 | 0.0877 | 0.0706 |  |  |  | 1 | 1.4675
144000 | 4 | 2 | 41230 | 4.7854 | 2.6047 | 0.0877 | 0.0881 |  |  |  | 2 | 2.5744
144000 | 2.8 | 1.5 | 43360 | 4.8731 | 2.6227 | 0.0877 | 0.018 |  |  |  | 3 | 3.6116
146960 | 3.1621 | 1.75 | 45880 | 4.9607 | 2.7108 | 0.0876 | 0.0881
149690 | 3.4597 | 1.8775 | 47770 | 5.0122 | 2.8014 | 0.0515 | 0.0906
154150 | 3.74 | 2.0536 | 48000 | 5.0691 | 2.8044 | 0.0569 | 0.003
158810 | 4.0203 | 2.3172 | 52000 | 5.1791 | 2.9369 | 0.11 | 0.13256
163470 | 4.3006 | 2.4585 | 56000 | 5.3291 | 3.0295 | 0.15 | 0.09256
168320 | 4.5984 | 2.6872 | 60000 | 5.4491 | 3.1221 | 0.12 | 0.09256
173170 | 4.7913 | 2.8809 | 64000 | 5.5591 | 3.2146 | 0.11 | 0.09256
177820 | 5.0366 | 3.1097 | 68000 | 5.6691 | 3.3072 | 0.11 | 0.09256
183060 | 5.247 | 3.251 | 70000 | 5.7591 | 3.3997 | 0.09 | 0.09256
187520 | 5.4398 | 3.3922 | After 2nd MI |  |  | Output Difference | Heat Rate Difference
192000 | 5.5977 | 3.4634 | 0 | 0.89215 | -0.13247
192000 | 5.207 | 3 | 2780 | 1.2776 | 0.20683 | 0.3854 | 0.3393
192000 | 5.003 | 2 | 3960 | 1.4701 | 0.36543 | 0.1925 | 0.1586
192000 | 3.2 | 1.8 | 8810 | 1.7854 | 0.54143 | 0.3153 | 0.176
|  |  | 12500 | 2.0132 | 0.80523 | 0.2278 | 0.2638
|  |  | 18510 | 2.3111 | 1.1042 | 0.2979 | 0.299
|  |  | 24330 | 2.609 | 1.3157 | 0.2979 | 0.2115
|  |  | 30740 | 2.9944 | 1.5274 | 0.3854 | 0.2117
|  |  | 36170 | 3.2223 | 1.6861 | 0.2279 | 0.1587
|  |  | 40630 | 3.4501 | 1.7675 | 0.2278 | 0.0814
|  |  | 43150 | 3.5553 | 1.8475 | 0.1052 | 0.08
|  |  | 47850 | 3.7422 | 1.9675 | 0.1869 | 0.12
|  |  | 48000 | 3.7922 | 1.9675 | 0.05 | 0
|  |  | 55000 | 4.0122 | 2.1875 | 0.22 | 0.22
|  |  | 60000 | 4.2322 | 2.3175 | 0.22 | 0.13
|  |  | 65000 | 4.4522 | 2.4475 | 0.22 | 0.13
|  |  | 70000 | 4.6722 | 2.5775 | 0.22 | 0.13
|  |  | After 3rd MI |  |  | Output Difference | Heat Rate Difference
|  |  | 0 | 2.2669 | 0.97445
|  |  | 2960 | 2.629 | 1.2244 | 0.3621 | 0.25
|  |  | 5690 | 2.9266 | 1.3519 | 0.2976 | 0.1275
|  |  | 10150 | 3.2069 | 1.528 | 0.2803 | 0.1761
|  |  | 14810 | 3.4872 | 1.7916 | 0.2803 | 0.2636
|  |  | 19470 | 3.7675 | 1.9329 | 0.2803 | 0.1413
|  |  | 24320 | 4.0653 | 2.1616 | 0.2978 | 0.2287
|  |  | 29170 | 4.2582 | 2.3553 | 0.1929 | 0.1937
|  |  | 33820 | 4.5035 | 2.5841 | 0.2453 | 0.2288
|  |  | 39060 | 4.7139 | 2.7254 | 0.2104 | 0.1413
|  |  | 43520 | 4.9067 | 2.8666 | 0.1928 | 0.1412
|  |  | 48000 | 5.0646 | 2.9378 | 0.1579 | 0.0712
|  |  | 55000 | 5.2669 | 3.1744 | 0.2023 | 0.2366
|  |  | 60000 | 5.4669 | 3.3244 | 0.2 | 0.15
|  |  | 65000 | 5.6169 | 3.4944 | 0.15 | 0.17
|  |  | 70000 | 5.7169 | 3.6144 | 0.1 | 0.12

## Input 2_ Calculation Sheet
Plant Performance Audit-1
ONGC Tripura Power Company Limited (OTPC)
2X363.3 MW Combined Cycle Power Plant, Tripura, India
Actual CC Output and Heat Rate Correction Curves up to 200000 FFH provided by OTPC
Degradation curve in Table form: |  |  | GT-2 | [10 empty] | GTs | MIs
[10 empty] | GT | MIs |  |  | GT-1 | 0
GT Fired Hours | Output Degradation | HR degradation | Input Data | [6 empty] | GT-1 | 0 |  |  | GT-2 | 1
0 | 0 | 0 | GTs | No. of MIs completed | 1st MI FFH | 2nd MI FFH | 3rd MI FFH | Current FFH |  | GT-2 | 1 |  |  |  | 2
1810 | 1.0147 | 0.2454 | GT-2 | 1 | 55489.8 | 0 | 0 | 60343.7 | 0 |  | 2 |  |  |  | 3
4160 | 1.4873 | 0.4734 | [8 empty] | 3
6880 | 1.7849 | 0.6666 | Output Calculations
9220 | 2.0125 | 0.71978 | FFH Before 1st MI | FFH after 1st MI | FFH after 2nd MI | FFH after 3rd MI | Current FFH
12330 | 2.2577 | 0.8603 | 55489.8 | 4853.9 | 60343.7 | 60343.7 | 60343.7
13690 | 2.3803 | 0.9659 |  | 60343.7 | 60343.7 | 60343.7
16790 | 2.573 | 1.0715 | [6 empty] | Performance Reset after MI as per Curve
19120 | 2.6956 | 1.1595 | Output Results | [5 empty] | 1st MI | Output reset |  | 2.3
21650 | 2.8708 | 1.2652 | No of MIs completed | Heat Rate Degradation Factor |  | Output Degradation Factor |  |  |  | Heatrate reset |  | 1.7521
23390 | 2.9584 | 1.3357 | 1 | 1.0443 |  | 2.6244 |  |  | 2nd MI | Output reset |  | 2.4
26500 | 3.1161 | 1.4415 | [7 empty] | Heatrate reset |  | 1.6
28820 | 3.2213 | 1.512 | GT Fired Hours | Output Degradation | HR degradation |  |  |  | 3rd MI | Output reset |  | 2.4
31730 | 3.3615 | 1.6353 | 0 | 0 | 0 |  |  |  |  | Heatrate reset |  | 1.6
33860 | 3.4317 | 1.7058 | 1810 | 1.0147 | 0.2454
36390 | 3.5893 | 1.7765 | 4160 | 1.4873 | 0.4734 | [7 empty] | Degradation Curve based on MI Hours
38130 | 3.642 | 1.8821 | 6880 | 1.7849 | 0.6666
40850 | 3.7472 | 1.9702 | 9220 | 2.0125 | 0.7197 |  |  |  | GT-2
42790 | 3.8523 | 2.0408 | 12330 | 2.2577 | 0.8603
45310 | 3.98 | 2.1638 | 13690 | 2.3803 | 0.9659 |  |  |  | Degradation Curve Reset Calculation |  | Degradation Factor wrt MI
47760 | 4.08 | 2.2 | 16790 | 2.573 | 1.0715
48000 | 4.1 | 2.2521 | 19120 | 2.6956 | 1.1595 |  |  |  | After 1st MI |  | Before MI
48000 | 3.7423 | 1.5 | 21650 | 2.8708 | 1.2652 |  |  |  | Output | Heat Rate | Output | Heat Rate
48000 | 1.8 | 0.5 | 23390 | 2.9584 | 1.3357 |  |  |  | 52000 | 52000 | 52000 | 52000
50010 | 1.9812 | 0.7661 | 26500 | 3.1161 | 1.4415 |  |  |  | 56000 | 56000 | 56000 | 56000
52740 | 2.2964 | 0.8716 | 28820 | 3.2213 | 1.512 |  |  |  | 4.268 | 2.3421 | 4.268 | 2.3421
55650 | 2.5065 | 0.9772 | 31730 | 3.3615 | 1.6353 |  |  |  | 4.442 | 2.4321 | 4.442 | 2.4321
57790 | 2.6817 | 1.0828 | 33860 | 3.4317 | 1.7058 |  |  |  | 4.4198 | 2.4206 | 4.4198 | 2.4206
60120 | 2.8743 | 1.2233 | 36390 | 3.5893 | 1.7765 |  |  |  | After 2nd MI |  | After 1st MI
62450 | 3.0144 | 1.3464 | 38130 | 3.642 | 1.8821 |  |  |  | Output | Heat Rate | Output | Heat Rate
65370 | 3.2246 | 1.4345 | 40850 | 3.7472 | 1.9702 |  |  |  | 4740 | 4740 | 4740 | 4740
67310 | 3.3647 | 1.5927 | 42790 | 3.8523 | 2.0408 |  |  |  | 7650 | 7650 | 7650 | 7650
69840 | 3.5399 | 1.6984 | 45310 | 3.98 | 2.1638 |  |  |  | 2.6162 | 1.0401 | 2.6162 | 1.0401
72360 | 3.6626 | 1.7516 | 47760 | 4.08 | 2.2 |  |  |  | 2.8263 | 1.1457 | 2.8263 | 1.1457
74690 | 3.8027 | 1.9269 | 48000 | 4.1 | 2.2521 |  |  |  | 2.6244 | 1.0443 | 2.6244 | 1.0443
77400 | 3.8904 | 2.0151 | 52000 | 4.268 | 2.3421 |  |  |  | After 3rd MI |  | After 2nd MI
79540 | 4.0481 | 2.1032 | 56000 | 4.442 | 2.4321 |  |  |  | Output | Heat Rate | Output | Heat Rate
81480 | 4.1357 | 2.2088 | 60000 | 4.556 | 2.5221 |  |  |  | 60000 | 60000 | 60000 | 60000
84380 | 4.2409 | 2.2446 | 64000 | 4.69 | 2.6121 |  |  |  | 65000 | 65000 | 65000 | 65000
86710 | 4.3286 | 2.3152 | 68000 | 4.884 | 2.7021 |  |  |  | 3.5644 | 1.8943 | 3.5644 | 1.8943
89230 | 4.4163 | 2.4033 | 70000 | 4.968 | 2.7921 |  |  |  | 3.7844 | 2.0243 | 3.7844 | 2.0243
91360 | 4.504 | 2.4213 | After 1st MI |  |  | Output Difference | Heat Rate Difference |  | 3.5796 | 1.9032 | 3.5796 | 1.9032
93880 | 4.5916 | 2.5094 | 0 | 2.1198 | 0.66852 | [5 empty] | After 3rd MI
95770 | 4.6431 | 2.6 | 2010 | 2.301 | 0.93462 | 0.1812 | 0.2661 |  |  |  | Output | Heat Rate
96000 | 4.7 | 2.605 | 4740 | 2.6162 | 1.0401 | 0.3152 | 0.1055 |  |  |  | 60000 | 60000
96000 | 3 | 1 | 7650 | 2.8263 | 1.1457 | 0.2101 | 0.1056 |  |  |  | 65000 | 65000
96000 | 2.3 | 1 | 9790 | 3.0015 | 1.2513 | 0.1752 | 0.1056 |  |  |  | 4.3796 | 2.6532
98780 | 2.6854 | 1.3393 | 12120 | 3.1941 | 1.3918 | 0.1926 | 0.1405 |  |  |  | 4.5296 | 2.8232
99960 | 2.8779 | 1.4979 | 14450 | 3.3342 | 1.5149 | 0.1401 | 0.1231 |  |  |  | 4.3899 | 2.6649
104810 | 3.1932 | 1.6739 | 17370 | 3.5444 | 1.603 | 0.2102 | 0.0881 |  |  |  | Results
108500 | 3.421 | 1.9377 | 19310 | 3.6845 | 1.7612 | 0.1401 | 0.1582 |  |  |  | Output Degradation
114510 | 3.7189 | 2.2367 | 21840 | 3.8597 | 1.8669 | 0.1752 | 0.1057 |  |  |  | 0 | 4.4198
120330 | 4.0168 | 2.4482 | 24360 | 3.9824 | 1.9201 | 0.1227 | 0.0532 |  |  |  | 1 | 2.6244
126740 | 4.4022 | 2.6599 | 26690 | 4.1225 | 2.0954 | 0.1401 | 0.1753 |  |  |  | 2 | 3.5796
132170 | 4.6301 | 2.8186 | 29400 | 4.2102 | 2.1836 | 0.0877 | 0.0882 |  |  |  | 3 | 4.3899
136630 | 4.8579 | 2.9 | 31540 | 4.3679 | 2.2717 | 0.1577 | 0.0881
139150 | 4.9631 | 2.98 | 33480 | 4.4555 | 2.3773 | 0.0876 | 0.1056 |  |  |  | HR Degradation
143850 | 5.15 | 3.1 | 36380 | 4.5607 | 2.4131 | 0.1052 | 0.0358 |  |  |  | 0 | 2.4206
144000 | 5.2 | 3.1 | 38710 | 4.6484 | 2.4837 | 0.0877 | 0.0706 |  |  |  | 1 | 1.0443
144000 | 4 | 2 | 41230 | 4.7361 | 2.5718 | 0.0877 | 0.0881 |  |  |  | 2 | 1.9032
144000 | 2.8 | 1.5 | 43360 | 4.8238 | 2.5898 | 0.0877 | 0.018 |  |  |  | 3 | 2.6649
146960 | 3.1621 | 1.75 | 45880 | 4.9114 | 2.6779 | 0.0876 | 0.0881
149690 | 3.4597 | 1.8775 | 47770 | 4.9629 | 2.7685 | 0.0515 | 0.0906
154150 | 3.74 | 2.0536 | 48000 | 5.0198 | 2.7715 | 0.0569 | 0.003
158810 | 4.0203 | 2.3172 | 52000 | 5.1298 | 2.9041 | 0.11 | 0.13256
163470 | 4.3006 | 2.4585 | 56000 | 5.2798 | 2.9966 | 0.15 | 0.09256
168320 | 4.5984 | 2.6872 | 60000 | 5.3998 | 3.0892 | 0.12 | 0.09256
173170 | 4.7913 | 2.8809 | 64000 | 5.5098 | 3.1818 | 0.11 | 0.09256
177820 | 5.0366 | 3.1097 | 68000 | 5.6198 | 3.2743 | 0.11 | 0.09256
183060 | 5.247 | 3.251 | 70000 | 5.7098 | 3.3669 | 0.09 | 0.09256
187520 | 5.4398 | 3.3922 | After 2nd MI |  |  | Output Difference | Heat Rate Difference
192000 | 5.5977 | 3.4634 | 0 | 0.22443 | -0.55575
192000 | 5.207 | 3 | 2780 | 0.60983 | -0.21645 | 0.3854 | 0.3393
192000 | 5.003 | 2 | 3960 | 0.80233 | -0.057846 | 0.1925 | 0.1586
192000 | 3.2 | 1.8 | 8810 | 1.1176 | 0.11815 | 0.3153 | 0.176
|  |  | 12500 | 1.3454 | 0.38195 | 0.2278 | 0.2638
|  |  | 18510 | 1.6433 | 0.68095 | 0.2979 | 0.299
|  |  | 24330 | 1.9412 | 0.89245 | 0.2979 | 0.2115
|  |  | 30740 | 2.3266 | 1.1042 | 0.3854 | 0.2117
|  |  | 36170 | 2.5545 | 1.2629 | 0.2279 | 0.1587
|  |  | 40630 | 2.7823 | 1.3443 | 0.2278 | 0.0814
|  |  | 43150 | 2.8875 | 1.4243 | 0.1052 | 0.08
|  |  | 47850 | 3.0744 | 1.5443 | 0.1869 | 0.12
|  |  | 48000 | 3.1244 | 1.5443 | 0.05 | 0
|  |  | 55000 | 3.3444 | 1.7643 | 0.22 | 0.22
|  |  | 60000 | 3.5644 | 1.8943 | 0.22 | 0.13
|  |  | 65000 | 3.7844 | 2.0243 | 0.22 | 0.13
|  |  | 70000 | 4.0044 | 2.1543 | 0.22 | 0.13
|  |  | After 3rd MI |  |  | Output Difference | Heat Rate Difference
|  |  | 0 | 1.1796 | 0.30319
|  |  | 2960 | 1.5417 | 0.55319 | 0.3621 | 0.25
|  |  | 5690 | 1.8393 | 0.68069 | 0.2976 | 0.1275
|  |  | 10150 | 2.1196 | 0.85679 | 0.2803 | 0.1761
|  |  | 14810 | 2.3999 | 1.1204 | 0.2803 | 0.2636
|  |  | 19470 | 2.6802 | 1.2617 | 0.2803 | 0.1413
|  |  | 24320 | 2.978 | 1.4904 | 0.2978 | 0.2287
|  |  | 29170 | 3.1709 | 1.6841 | 0.1929 | 0.1937
|  |  | 33820 | 3.4162 | 1.9129 | 0.2453 | 0.2288
|  |  | 39060 | 3.6266 | 2.0542 | 0.2104 | 0.1413
|  |  | 43520 | 3.8194 | 2.1954 | 0.1928 | 0.1412
|  |  | 48000 | 3.9773 | 2.2666 | 0.1579 | 0.0712
|  |  | 55000 | 4.1796 | 2.5032 | 0.2023 | 0.2366
|  |  | 60000 | 4.3796 | 2.6532 | 0.2 | 0.15
|  |  | 65000 | 4.5296 | 2.8232 | 0.15 | 0.17
|  |  | 70000 | 4.6296 | 2.9432 | 0.1 | 0.12